## Slide 2: Integration of solar process heat at a South African microbrewery: a feasibility study
Pieter De Wet Taljaard a, Thomas Harms a, and Ben Sebitosi b
a Solar Thermal Energy Research Group (STERG),
Stellenbosch University
b Department of mechanical and mechatronic engineering,
Stellenbosch University

## Slide 3: Background
SA Solar Resource in Industrial Areas
Gauteng
2000 kWh/m2
Greater Cape Town
1800 kWh/m2
Greater Durban
1600 kWh/m2

## Slide 4: Background
Industrial Heat demand
Hess 2015, (Adapted from SATIM 2014)
Sectoral Energy Demand
Industrial Energy Usage
Fuel Source

## Slide 5: Background
Technology
Temperature
Supplied
Stationary vs
Tracking

## Slide 6: Background
Target industries
Low temperature heat requirement
Constant heat demand
High cost fuel source
Food and beverage, Textile and agri-processing

## Slide 7: Background
Berg River Brewery
Microbrewery in Paarl, WC
Established in 2016
Food and Beverage Industry
Low to medium Temperature requirement

## Slide 8: Motivation
SPH at BRB
Unbiased assessment of SPH
SPH for small industrial applications

## Slide 9: Thermal Demand
Per Brew
Process | Start Temp. [°C] | End Temp. [°C] | Medium | Specific heat [kWh/m3K] | Volume [L] | Heat Requirement [kWhth] | Percentage of Heat Requirement
Mashing | 18 | 75 | water | 1.16 | 300 | 19.8 | 23%
Wort filter | 18 | 75 | water | 1.16 | 350 | 23.1 | 26%
Boiler/Kettle | 75 | 100 | sweet wort | 1 | 600 | 15.0 | 17%
Boiling/Hot hold | 100 | 100 | wort & hops | 1.25 | 600 | 30.0 | 34%

## Slide 10: Thermal Demand
Load Profile
3 Brews per day
3 Brewing days per
Brewing week
Seasonal production variation
Summer vs Winter

## Slide 11: System Design
Concept
External heat
exchangers
Heat recovery
Preheating strategy
Backup System

## Slide 12: System Design
Collector location
North: 180 m2 - 23°
South: 250 m2 - 21°

## Slide 13: System Design
Collector location
North: 180 m2 - 23°
South: 250 m2 - 21°
Asbestos Roof!!!

## Slide 14: System Design
Specifics
Collector Aperture Area: 18.42 m2
Storage Volume: 1500 L
VSD drives on Solar and tank loops
Stainless steel food grade components

## Slide 15: System Performance Modelling
Input
Solar resource
Process characteristics
Heat demand type
SolGain demand profile

## Slide 16: System Performance Modelling
Results
Annual Thermal Demand
27 170 kWhth
Supplied by SPH
19 020 kWhth
Solar Fraction - 70%
System Efficiency – 27%
Chart: System Production
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Qsolar | 2219.7821 | 2208.7847 | 1613.6731 | 750.3157 | 1068.3858 | 522.7044 | 621.1935 | 1055.385 | 1620.0917 | 2352.3403 | 2500.9563 | 2433.4112
Qconv | 270.8012 | 508.2153 | 650.4936 | 608.1843 | 969.3642 | 835.7956 | 737.3065 | 982.365 | 1096.9083 | 817.493 | 442.4604 | 283.5888
Solar fraction | 0.89127 | 0.81295 | 0.7127 | 0.55231 | 0.5243 | 0.38477 | 0.45726 | 0.51792 | 0.59628 | 0.7421 | 0.84968 | 0.89562

## Slide 17: Business Case – To Buy or not to Buy
Capex
Chart: SPH System Component Specific Cost
| Collectors | HE, pumps and control | Piping | Installation | Maintenance | Roof strengthning | Storage
Minimum | 1989 | 918 | 1224 | 765 | 459 | 1071 | 1683
BRB | 3477.2286 | 6536.24 | 3062.7769 | 2886.4542 | 747.012 | 1002.241 | 3086.2724
Maximum | 5508 | 6120 | 5661 | 3213 | 1377 | 1683 | 8109
System Cost
R 20 800/m2
Minimum
R 16 000/m2
Maximum
R31 600/m2

## Slide 18: Business Case – To Buy or not to Buy
LCOH
Period | LCOH - R/kWhth
10 years | R 3.43
20 Years | R 2.62
Discount Rate: 4.8%
Degradation: 0.5%
O&M Cost: R 15 000/annum

## Slide 19: Business Case – To Buy or not to Buy
LCOH
Period | LCOH - R/kWhth
10 years | R 3.43
20 Years | R 2.62
Discount Rate: 4.8%
Degradation: 0.5%
O&M Cost: R 15 000/annum
Electricity Cost : R1.775 R/kWh

## Slide 20: Business Case – To Buy or not to Buy
Payback Period
Berg River Brewery – 12.4 Years
CBC system – 9.3 Years

## Slide 21: Business Case – To Buy or not to Buy
Conclusion
Low system utilisation
Low Electricity cost
High system cost

## Slide 22: Business Case – To Buy or not to Buy
Conclusion
Low system utilisation
Low Electricity cost
High system cost
Investigate suitability of alternative technologies
Not Economically Feasible

## Slide 23: Thank You
Berg River Brewery
NRF
STERG
STERG@sun.ac.za
+27 (0)21 808 4016